### UNDERGROUND STORAGE TANK PROGRAM

#### REPAIR/MODIFICATION CLASSIFICATIONS

Work Requiring a Major Modification Permit:

Any work that requires more than one inspection by Yolo County Environmental Health UST Staff should be classified as a major modification. This work includes any type of repair/modification that will require soil/groundwater sampling. Examples of major modifications include (but are not limited to):

- Piping upgrades

- Any piping repairs

- Lining repairs/installations/inspections

- Tank shell repairs

- Sump replacements

- Under-Dispenser Containment replacements

Work Requiring a Minor Modification Permit:

Any UST work to be completed that will require only one inspection by Yolo County Environmental Health Staff should be considered a minor modification. No work requiring sampling of soil or groundwater should be considered a minor modification. Some examples include:

- Replacement of a direct-bury spill container

- Installation of a new monitoring system or console

- Replacement of any monitoring equipment with a “non-like” item

- Repair/replacement of cathodic protection equipment

- Installation of new overfill prevention system

- Installing new dispensers

Work Not Requiring a Permit but Requiring Submittal of Description of Repair Work Completed:

The following repairs/modifications do not require a permit from Yolo County Environmental Health. However any repairs completed require the submittal of the “Description of Repair Work Completed” form:

- Replacing a spill container that is contained in a sump

- Replacing a drop tube

- Replacing sensors “like for like”

- Replacing an automatic line leak detector “like for like”

- Repairing/Replacing test boots

- Replacing a turbine “like for like”

### UNDERGROUND STORAGE TANK PROGRAM

#### Blueprints and Parts List Requirements

**This list is not intended to be all-inclusive, it is meant to act as a guide for what should be included in drawings submitted to Yolo County Environmental Health. A parts list is to be included on the drawings and should include make & model number and correspond to side view or end view drawings by number or letter.

Overhead View of Site (Drawn to scale and to include all of following that apply):

____	North arrow

____	Scale of drawing

____  	Closest landmarks (e.g. buildings, streets, etc)

____	Bollards or guard posts

____  	Dispenser islands

____	Tanks

____	Tank excavation

____	All piping that will contain product (supply & return)

____	Vapor recovery piping

____	Vent piping & termination

____	Buildings

____	Location of leak detection/monitoring panel

____	Location of Emergency Shutoff

____	Location of any proposed or existing wells (observation, monitor, etc.)

____	Location of overfill alarm

____	Indicate slope on piping toward tank (must be minimum of 1/8 inch per foot)

____	Tank vent termination

##### Side view of all that apply to scope of work

###### End View of Pipe Trench

____	Type of piping (i.e., rigid FRP, Enviroflex, etc.)

____	Piping trenches showing distances between pipes, from pipes to bottom of trench, pipes to side of trench, pipes to surface. Also include backfill material and type/thickness of cap over trench. Must be a minimum of twice the piping diameter between lines and a minimum of 6 inches between side of trench and pipe on each side.

Side View of Pipe Transitions and Penetrations

____	Penetration of underground piping into basement or to ground surface – Include the pipe or collar that provides a conduit for the double wall pipe

____	Underground caps, plugs & sealants (to make penetration watertight)

____	Termination assembly – Include termination plug, seals & test donuts, as well as termination of secondary underground piping & test boots/end boots

____ 	Transition from flexible or fiberglass piping to above ground piping – Include protection from sunlight & elements, as well as construction of above ground piping

____	Transition sumps, containment boxes, sensors and ball valves (if any)

Side View of Sumps

____	Method of attachment of sump to tank

____	Penetration in sumps (boots, flanges, fittings)

____	Piping as it goes through penetrations

____	Termination of secondary walls of pipe in sump

____	Location of test boots

____	All piping & connections inside sump

____	All other equipment inside sump

____	Sump sensor

____	Spill containment buckets

____	Lids to manways

____	Type & depth of fill materials, and cap

____	Line Leak Detector

SUMP INSTALLATION INCLUDE A BLOWUP DRAWING ENCOMPASSING:

____	Manway Lid

____	Manway Skirt

____	Sump

____	Sump Lid

____	Spill Buckets

____	Sump Top Hat

____	Interface between the manway skirt and sump top hat

____	Interface or connection between spill buckets

Side View of Under Dispenser Containment

____	Penetrations into pans (depict type of penetration fitting)

____	All piping & conduits as they go through penetrations

____	Termination of secondary walls of pipe inside under dispenser containment

____	Shear valves

____	Attachment of pipes, etc to pan infrastructure

____	Floats or sensors

____	Type of UDC (Bravo, FRP, shallow, deep, etc.)

____	Any other equipment inside UDC

____	Flex connectors and boots

Side View of Tank & Excavation

____	Size of tank in gallons

____	Dimensions of excavation & tank

____ 	Distance from ends & sides of tank(s) to sidewalls of excavation

____	Depth of backfill beneath tanks & above tanks

____	Type & thickness of cap above tank

____	Sumps

____	Spill buckets & lids

____ 	All other sumps or bungs on tank

____	Risers

____	Location of ATG (Tank level monitor)

____	Turbines

____	Compartments in tank

____	Drop tube

____	Overfill prevention devices

____	Any slabs or deadmen with location and type of tie down straps

____	Level or slope of tank

____	Any other equipment

____	Any other items in close proximity to UST (e.g., monitoring wells, etc)

____	Location of interstitial monitor

____	Certification by a registered engineer that groundwater conditions do not warrant additional engineering to counteract tank buoyancy (Alternative: Attach buoyancy calculations stamped by a registered engineer based upon the assumption that each tank lies completely submerged)

### UNDERGROUND STORAGE TANK PROGRAM

#### DESCRIPTION OF REPAIR WORK COMPLETED

This form is to be completed by the service technician or contractor anytime a repair or modification is made to an underground storage tank system in Yolo County that does not require a repair/modification permit from the Yolo County Environmental Health Department. Please complete and submit within 5 business days of the repair. If you are unsure if the work to be completed requires a permit please call the UST program manager at (530) 666-8646.

FACILITY/SITE INFORMATION

Facility Name: __________________________________________  Phone No.: ___________________

Facility Address: ______________________________________________________________________

Owner’s Name: _________________________________________  Phone No.: ____________________

Owner’s Address: ______________________________________________________________________

CONTRACTOR INFORMATION

Contractors Name: _______________________________________  Phone No.: ___________________

Contractor Address: ____________________________________________________________________

Company Name: _____________________________________  Lic. Type/No.: ____________________

DESCRIPTION OF WORK COMPLETED: (Please include all parts repaired/replaced with applicable model numbers, location of sensors, etc.  Attach applicable site maps, cut sheets, etc.)

______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Was testing done to confirm the parts repaired/replaced operational?   YES        NO

*Please attach all test results to this form

__________________________________________		___________		Date Work Completed:

Contractors Signature						Date

____________________

__________________________________________		___________

Received By							Date