## Slide 1
Wild Wings County Service Area
Water Supply Update
July 7, 2021

## Slide 2: Topics
Summary of water shortage issues
Plan for changing Pumps
Considerations for replacement well

## Slide 3: Photo of Sierra Nevada’s April 2021
Lake Tahoe
Dismal snow-pack

## Slide 4: Hydrologic Cycle

## Slide 5: Map of Wild Wings Water System

## Slide 6: Illustration of Wild Wings Wells

## Slide 7: Canvas Back Depth to Water
Pump Drawdown
Static Water Level
50 feet deeper than 2020
65 feet deeper than 2019
210’
160’
145’

## Slide 8: Canvas Back Water Supply
Canvas Back is used for irrigation supply and is a backup for Pintail for the Potable Water System.
Water Levels are lowest ever for this time of year
  Typical Spring/Fall levels are 120 feet – 160 feet deep
  Current level is 210 feet deep as of July 1, 2021
  Levels are falling about 1-2 ft per day
The existing pump cannot supply water at these deeper levels.
A new pump was selected to increase water supply from the well. Limited pumps were available due to increased demand and supply chain impacts.

## Slide 9: Canvas Back New Pump
Today’s Operation
Historical
Operation
Selected Pump
Existing Pump

## Slide 10: Pintail Depth to Water
Static Water Level
Pump Drawdown
205’
45 feet deeper than 2020
160’
60 feet deeper than 2019
145’

## Slide 11: Pintail Water Supply
Pintail is the primary well for the Potable Water System.
Water Levels are lowest ever for this time of year
  Typical Spring/Fall levels are 120 feet – 160 feet deep
  Current level is 205 feet deep as of July 1, 2021
  Levels are falling about 0.5-1.5 ft per day
The existing pump will not meet the minimum Potable Water demand if water levels continue dropping.
A new pump was selected to increase water supply from the well. Limited pumps were available due to increased demand and supply chain impacts.

## Slide 12: Pintail New Pump
Today’s Operation
Historical
Operation
Selected Pump
Existing Pump

## Slide 13: Plan for Changing Pumps
Canvas Back
  New pump is expected to be installed by next week.
  Pump will make about 700-900 gpm in current conditions.
  A deeper replacement well is being considered, if levels continue declining
Pintail
  New pump may be available within 2 weeks.
  Lower pump from 380 to 500 ft.
  Pump will make about 650-850 gpm in current conditions.

## Slide 14: What you can do to help
Conserving water to reduce peak use will help ensure the wells can meet the water demands through the summer.
Nearly 50% of water use in the summer is for outdoor landscaping.
Chart: Wildwings Water Usage
| April | May | June | July
2019 | 3.25 | 5.75 | 6.53 | 11.18
2020 | 5.56 | 7.31 | 10.39 | 12.6
2021 | 4.22 | 7 | 7.47 | 10.47

## Slide 15: Considerations for Replacement Well (Canvas Back)
  Site Constraints
  Hydrogeology
  Cost
  Schedule